{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["监督性监测废气数据"],"not_rendered":{"external_links":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"监督性监测废气数据","index":0,"n_rows":19,"n_cols":20,"rows_kept":19,"flags":["formulas_cached_only"]}
["行政区代码","行政区","组织机构代码","统一社会信用代码","企业名称","监测日期","监测点名称","监测项目名称","标准名称","条目名称","温度","含氧量","实测浓度","折算浓度","监测限值","监测单位","超标倍数","是否达标","废气排放量","工况负荷"]
["150300","乌海市海南区","","91150300772232426Y","内蒙古蒙电华能热电股份有限公司乌海发电厂","2022-06-21","5号机组排放口","烟尘","火电厂大气污染物排放标准(GB13223-2011)","（表2）大气污染物特别排放限值/烟囱或烟道/燃煤锅炉","63.6","6.9","3.8","4.0","20","mg/m3","--","是","912371","73"]
["150300","乌海市海南区","","91150300772232426Y","内蒙古蒙电华能热电股份有限公司乌海发电厂","2022-06-21","6号机组排放口","烟尘","火电厂大气污染物排放标准(GB13223-2011)","（表2）大气污染物特别排放限值/烟囱或烟道/燃煤锅炉","62.4","6.6","3.5","3.7","20","mg/m3","--","是","875898","77"]
["150300","乌海市海南区","","91150300772232426Y","内蒙古蒙电华能热电股份有限公司乌海发电厂","2022-06-21","5号机组排放口","二氧化硫","火电厂大气污染物排放标准(GB13223-2011)","（表2）大气污染物特别排放限值/烟囱或烟道/燃煤锅炉","63.6","6.9","<3","<3","50","mg/m3","--","是","912371","73"]
["150300","乌海市海南区","","91150300772232426Y","内蒙古蒙电华能热电股份有限公司乌海发电厂","2022-06-21","6号机组排放口","二氧化硫","火电厂大气污染物排放标准(GB13223-2011)","（表2）大气污染物特别排放限值/烟囱或烟道/燃煤锅炉","62.4","6.6","<3","<3","50","mg/m3","--","是","875898","77"]
["150300","乌海市海南区","","91150300772232426Y","内蒙古蒙电华能热电股份有限公司乌海发电厂","2022-06-21","6号机组排放口","氮氧化物","火电厂大气污染物排放标准(GB13223-2011)","（表2）大气污染物特别排放限值/烟囱或烟道/燃煤锅炉","62.4","6.6","29","30","100","mg/m3","--","是","875898","77"]
["150300","乌海市海南区","","91150300772232426Y","内蒙古蒙电华能热电股份有限公司乌海发电厂","2022-06-21","5号机组排放口","氮氧化物","火电厂大气污染物排放标准(GB13223-2011)","（表2）大气污染物特别排放限值/烟囱或烟道/燃煤锅炉","63.6","6.9","35","38","100","mg/m3","--","是","912371","73"]
["150300","乌海市海南区","","91150303752596628T","乌海市宏阳焦化有限责任公司","2022-06-08","1号2号焦炉脱硫塔排放口","氮氧化物","炼焦化学工业污染物排放标准(GB16171-2012)","（表6）大气污染物特别排放限值/焦炉烟囱","59.2","12.2","130","130","150","mg/m3","--","是","81725","55"]
["150300","乌海市海南区","","91150303752596628T","乌海市宏阳焦化有限责任公司","2022-06-08","1号2号焦炉脱硫塔排放口","二氧化硫","炼焦化学工业污染物排放标准(GB16171-2012)","（表6）大气污染物特别排放限值/焦炉烟囱","59.2","12.2","<3","<3","30","mg/m3","--","是","81725","55"]
["150300","乌海市海南区","","91150303752596628T","乌海市宏阳焦化有限责任公司","2022-06-08","1号2号焦炉脱硫塔排放口","颗粒物","炼焦化学工业污染物排放标准(GB16171-2012)","（表6）大气污染物特别排放限值/焦炉烟囱","59.2","12.2","3.1","3.1","15","mg/m3","--","是","81725","55"]
["150300","乌海市海南区","","91150303776102178K(  )","乌海市华资煤焦有限公司","2022-06-06","1号2号焦炉大烟囱排放口","颗粒物","炼焦化学工业污染物排放标准(GB16171-2012)","（表6）大气污染物特别排放限值/焦炉烟囱","270.9","15","11.2","11.2","15","mg/m3","--","是","236043","80"]
["150300","乌海市海南区","","91150303776102178K(  )","乌海市华资煤焦有限公司","2022-06-06","1号2号焦炉大烟囱排放口","氮氧化物","炼焦化学工业污染物排放标准(GB16171-2012)","（表6）大气污染物特别排放限值/焦炉烟囱","270.9","15","49","49","150","mg/m3","--","是","236043","80"]
["150300","乌海市海南区","","91150303776102178K(  )","乌海市华资煤焦有限公司","2022-06-06","1号2号焦炉大烟囱排放口","二氧化硫","炼焦化学工业污染物排放标准(GB16171-2012)","（表6）大气污染物特别排放限值/焦炉烟囱","270.9","15","<3","<3","30","mg/m3","--","是","236043","80"]
["150300","乌海市海南区","","","乌海市泰和煤焦化集团有限公司","2022-06-09","1号2号焦炉脱硫塔排放口","颗粒物","炼焦化学工业污染物排放标准(GB16171-2012)","（表6）大气污染物特别排放限值/焦炉烟囱","63.2","11.1","2.6","2.6","15","mg/m3","--","是","137252","49"]
["150300","乌海市海南区","","","乌海市泰和煤焦化集团有限公司","2022-06-09","1号2号焦炉脱硫塔排放口","二氧化硫","炼焦化学工业污染物排放标准(GB16171-2012)","（表6）大气污染物特别排放限值/焦炉烟囱","63.2","11.1","<3","<3","30","mg/m3","--","是","137252","49"]
["150300","乌海市海南区","","","乌海市泰和煤焦化集团有限公司","2022-06-09","1号2号焦炉脱硫塔排放口","氮氧化物","炼焦化学工业污染物排放标准(GB16171-2012)","（表6）大气污染物特别排放限值/焦炉烟囱","63.2","11.1","144","144","150","mg/m3","--","是","137252","49"]
["150300","乌海市海南区","","91150300674364222G","乌海市西部煤化工有限责任公司","2022-06-07","1号2号焦炉大烟囱排放口","氮氧化物","炼焦化学工业污染物排放标准(GB16171-2012)","（表6）大气污染物特别排放限值/焦炉烟囱","237.5","9.2","137","137","150","mg/m3","--","是","145429","75"]
["150300","乌海市海南区","","91150300674364222G","乌海市西部煤化工有限责任公司","2022-06-07","1号2号焦炉大烟囱排放口","二氧化硫","炼焦化学工业污染物排放标准(GB16171-2012)","（表6）大气污染物特别排放限值/焦炉烟囱","237.5","9.2","<3","<3","30","mg/m3","--","是","145429","75"]
["150300","乌海市海南区","","91150300674364222G","乌海市西部煤化工有限责任公司","2022-06-07","1号2号焦炉大烟囱排放口","颗粒物","炼焦化学工业污染物排放标准(GB16171-2012)","（表6）大气污染物特别排放限值/焦炉烟囱","237.5","9.2","7.0","7.0","15","mg/m3","--","是","145429","75"]